## Models Covered
THIS LOGBOOK ONLY COVERS THE MODELS BELOW
MODEL | DATA BOOK
PURY-M-YXM-A | MEES25K054
PURY-EM-YXM-A | MEES25K056
PUHY-M-YXM-A | MEES25K055
PUHY-EM-YXM-A | MEES25K057

## Site & System Details
Contractor & Site Details
Installation Contractor | Contractors Address | Site Name | Site Address
System & Installation Details
PURY System Model
PUHY System Model
System Reference
| Outdoor Unit 1 | Outdoor Unit 2 | Outdoor Unit 3
Model Number
Serial Number
M-NET Address
Outdoor Unit Location
Commissioning Date
Commissioning Engineer
Notes

## Indoor Details
Unit Number | M-Net Address | Indoor Unit Model | Indoor Unit Serial | Indoor Unit Location | M-NET RC Address (if applicable) | TH21 temp in Cooling Mode | TH22 temp in Cooling Mode | TH21 temp in Heating Mode | TH22 temp in Heating Mode
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
41
42
43
44
45
46
47
48
49
50

## BC & Sub Controllers
Unit | Model Number | Serial Number | M-NET Address
BC Controller (Main)
BC Controller (Sub 1)
BC Controller (Sub 2)
BC Controller (Sub 3)
BC Controller (Sub 4)
BC Controller (Sub 5)
BC Controller (Sub 6)
BC Controller (Sub 7)
BC Controller (Sub 8)
BC Controller (Sub 9)
BC Controller (Sub 10)
BC Controller (Sub 11)
Note: In order for PURY Ref Charge Calculation to work, the BC information needs to be completed.

## PURY YXM Ref Charge Calculation
PURY-YXM
Outdoor Unit | 0 |  |  |  | Piping Length from Outdoor unit to furthest indoor unit
| Connected Indoor Units |  |  |  | Pipe Work | [7 empty] | Factor |  |  | Index |  | Outdoor | Pre-Charge | Maximum Allowable
| Size | P*FY Series | Size | M*Z Series | Diameter | Length (m) | Type | Factor |  | Charge | Charge Calculation Results |  | <=30.5 |  | 0 | <80 | 1.8 | PURY-M200YXM | 8 | 31
| 10 |  | 15 |  | 1 1/8" - 28.58mm |  | High Pressure Gas | 0.32 | kg/m | 0 |  |  | 1 1/8" - 28.58mm | 0.32 | 81 | 81-160 | 2.3 | PURY-M250YXM | 8 | 35.4
| 15 |  | 20 |  | 7/8" - 22.2mm |  | High Pressure Gas | 0.2 | kg/m | 0 | Additional Charge | 1.8 | 7/8" - 22.2mm | 0.2 | 161 | 161-290 | 2.7 | PURY-M300YXM | 8 | 36.3
| 20 |  | 22 |  | 3/4" - 19.05mm |  | High Pressure Gas | 0.14 | kg/m | 0 | Outdoor Pre-Charge | #N/A | 3/4" - 19.05mm | 0.14 | 291 | 291-390 | 3.2 | PURY-M350YXM | 9.3 | 37.2
| 25 |  | 25 |  | 5/8" - 15.88mm |  | High Pressure Gas | 0.099 | kg/m | 0 | Total System Charge | #N/A | 5/8" - 15.88mm | 0.099 | 391 | 391-510 | 4.1 | PURY-M400YXM | 9.3 | 37.9
| 32 |  | 35 |  | 3/4" - 19.05mm |  | Liquid | 0.26 | kg/m | 0 |  |  | 3/4" - 19.05mm | 0.26 | 511 | 511-630 | 4.5 | PURY-M450YXM | 9.3 | 37.9
| 40 |  | 42 |  | 5/8" - 15.88mm |  | Liquid | 0.17 | kg/m | 0 | Maximum Allowable | #N/A | 5/8" - 15.88mm | 0.17 | 631 | 631-710 | 5.4 | PURY-M500YXM | 9.3 | 37.9
| 50 |  | 50 |  | 1/2" - 12.7mm |  | Liquid | 0.11 | kg/m | 0 |  |  | 1/2" - 12.7mm | 0.11 | 711 | 711-800 | 7.2 | PURY-M400YSXM | 16 | 58.6
| 63 |  | 60 |  | 3/8" - 9.52mm |  | Liquid | 0.054 | kg/m | 0 |  |  | 3/8" - 9.52mm | 0.054 | 801 | 801-890 | 8.1 | PURY-M450YSXM | 16 | 59.5
| 80 |  | 71 |  | 1/4" - 6.35mm |  | Liquid | 0.02 | kg/m | 0 |  |  | 1/4" - 6.35mm | 0.02 | 891 | 891-1070 | 9 | PURY-M500YSXM | 16 | 61.3
| 100 |  | 80 |  | Total Length | 0 | Meters | Pipe Work Additional |  | 0 |  |  |  |  | 1071 | 1071-1250 | 10.8 | PURY-M550YSXM | 16 | 62.2
| 125 | [11 empty] | >30.5 |  | 1251 | 1251 > | 12.6 | PURY-M600YSXM | 16 | 62.6
| 140 | [11 empty] | 1 1/8" - 28.58mm | 0.3 |  |  |  | PURY-M650YSXM | 17.3 | 62.6
| 200 |  |  |  | No of Main & Sub BC | [7 empty] | 7/8" - 22.2mm | 0.19 |  |  |  | PURY-M700YSXM | 18.6 | 62.8
| 250 |  |  |  | Main | 0 | [6 empty] | 3/4" - 19.05mm | 0.13 |  |  |  | PURY-M750YSXM | 18.6 | 62.8
[5 empty] | Sub | 0 | [6 empty] | 5/8" - 15.88mm | 0.09 |  |  |  | PURY-M800YSXM | 18.6 | 63.9
Total Index |  | 0 |  |  | Additional Charge | 0 | [6 empty] | 3/4" - 19.05mm | 0.24 |  |  |  | PURY-M850YSXM | 18.6 | 64
[13 empty] | 5/8" - 15.88mm | 0.16 |  |  |  | PURY-M900YSXM | 18.6 | 64.5
Index Charge |  | 1.8 | [10 empty] | 1/2" - 12.7mm | 0.1 |  |  |  | PURY-M950YSXM | 18.6 | 65.1
NOTE: | [12 empty] | 3/8" - 9.52mm | 0.05 |  |  |  | PURY-M1000YSXM | 18.6 | 65.3
- | Add Indoor Index Sizes, HPG & Liquid Pipe Lengths plus Piping Length of furthest indoor unit to populate Ref Calc.
- | When connecting following models, please contact Technical Helpdesk to clarify the additional charge. | [11 empty] | 1/4" - 6.35mm | 0.018 |  |  |  | PURY-EM200YXM | 5.3 | 31
| PEFY-M50/63VMA(L)-A1 | [16 empty] | PURY-EM250YXM | 5.3 | 35.4
| PEFY-MS71VMA(L)-A1 | [16 empty] | PURY-EM300YXM | 5.3 | 36.3
| PLFY-50/63VEM6-E | [16 empty] | PURY-EM350YXM | 6.3 | 37.2
| PLFY-M71VEM6-E | [16 empty] | PURY-EM400YXM | 6.3 | 37.9
[18 empty] | PURY-EM450YXM | 6.3 | 37.9
[18 empty] | PURY-EM500YXM | 6.3 | 37.9
[18 empty] | PURY-EM400YSXM | 10.6 | 58.6
[18 empty] | PURY-EM450YSXM | 10.6 | 59.5
[18 empty] | PURY-EM500YSXM | 10.6 | 61.3
[18 empty] | PURY-EM550YSXM | 10.6 | 62.2
[18 empty] | PURY-EM600YSXM | 10.6 | 62.6
[18 empty] | PURY-EM650YSXM | 11.6 | 62.6
[18 empty] | PURY-EM700YSXM | 12.6 | 62.8
[18 empty] | PURY-EM750YSXM | 12.6 | 62.8
[18 empty] | PURY-EM800YSXM | 12.6 | 63.9
[18 empty] | PURY-EM850YSXM | 12.6 | 64
[18 empty] | PURY-EM900YSXM | 12.6 | 64.5
[18 empty] | PURY-EM950YSXM | 12.6 | 65.1
[18 empty] | PURY-EM1000YSXM | 12.6 | 65.3
PURY-M200YXM
PURY-M250YXM
PURY-M300YXM
PURY-M350YXM
PURY-M400YXM
PURY-M450YXM
PURY-M500YXM
PURY-EM200YXM
PURY-EM250YXM
PURY-EM300YXM
PURY-EM350YXM
PURY-EM400YXM
PURY-EM450YXM
PURY-EM500YXM
PUHY-M200YXM
PUHY-M250YXM
PUHY-M300YXM
PUHY-M350YXM
PUHY-M400YXM
PUHY-M450YXM
PUHY-M500YXM

## PUHY YXM Ref Charge Calculation
PUHY-YXM
Outdoor Unit | 0 |  |  |  | Piping Length from Outdoor unit to furthest indoor unit
| Connected Indoor Units |  |  |  | Pipe Work | [7 empty] | Factor |  |  | Index |  | Outdoor | Pre-Charge | Maximum Allowable
| Size | P*FY Series | Size | M*Z Series | Diameter | Length (m) | Type | Factor |  | Charge | Charge Calculation Results |  | <=30.5 |  | 0 | <80 | 1.8 | PUHY-M200YXM | 8 | 26.5
| 10 |  | 15 |  | 3/4" - 19.05mm |  | Liquid | 0.26 | kg/m | 0 |  |  | 3/4" - 19.05mm | 0.26 | 81 | 81-160 | 2.3 | PUHY-M250YXM | 8 | 32.5
| 15 |  | 20 |  | 5/8" - 15.88mm |  | Liquid | 0.17 | kg/m | 0 | Additional Charge | 1.8 | 5/8" - 15.88mm | 0.17 | 161 | 161-290 | 2.7 | PUHY-M300YXM | 8 | 32.5
| 20 |  | 22 |  | 1/2" - 12.7mm |  | Liquid | 0.11 | kg/m | 0 | Outdoor Pre-Charge | #N/A | 1/2" - 12.7mm | 0.11 | 291 | 291-390 | 3.2 | PUHY-M350YXM | 9.3 | 34.7
| 25 |  | 25 |  | 3/8" - 9.52mm |  | Liquid | 0.054 | kg/m | 0 | Total System Charge | #N/A | 3/8" - 9.52mm | 0.054 | 391 | 391-510 | 4.1 | PUHY-M400YXM | 9.3 | 34.7
| 32 |  | 35 |  | 1/4" - 6.35mm |  | Liquid | 0.02 | kg/m | 0 |  |  | 1/4" - 6.35mm | 0.02 | 511 | 511-630 | 4.5 | PUHY-M450YXM | 9.3 | 34.7
| 40 |  | 42 |  | Total Length | 0 | Meters | Pipe Work Additional |  | 0 | Maximum Allowable | #N/A |  |  | 631 | 631-710 | 5.4 | PUHY-M500YXM | 9.3 | 34.7
| 50 |  | 50 | [9 empty] | >30.5 |  | 711 | 711-800 | 7.2 | PUHY-M400YSXM | 16 | 43.6
| 63 |  | 60 | [9 empty] | 3/4" - 19.05mm | 0.24 | 801 | 801-890 | 8.1 | PUHY-M450YSXM | 16 | 53
| 80 |  | 71 | [9 empty] | 5/8" - 15.88mm | 0.16 | 891 | 891-1070 | 9 | PUHY-M500YSXM | 16 | 53
| 100 |  | 80 | [9 empty] | 1/2" - 12.7mm | 0.1 | 1071 | 1071-1250 | 10.8 | PUHY-M550YSXM | 16 | 53
| 125 | [11 empty] | 3/8" - 9.52mm | 0.05 | 1251 | 1251 > | 12.6 | PUHY-M600YSXM | 16 | 53
| 140 | [11 empty] | 1/4" - 6.35mm | 0.018 |  |  |  | PUHY-M650YSXM | 17.3 | 53
| 200 | [16 empty] | PUHY-M700YSXM | 18.6 | 53.5
| 250 | [16 empty] | PUHY-M750YSXM | 18.6 | 53.5
[18 empty] | PUHY-M800YSXM | 18.6 | 53.7
Total Index |  | 0 | [15 empty] | PUHY-M850YSXM | 18.6 | 54
[18 empty] | PUHY-M900YSXM | 18.6 | 54.1
Index Charge |  | 1.8 | [15 empty] | PUHY-M950YSXM | 18.6 | 54.1
NOTE: | [17 empty] | PUHY-M1000YSXM | 18.6 | 54.1
- | Add Indoor Index Sizes, Liquid Pipe Length plus Piping Length of furthest indoor unit to populate Ref Calc.
- | When connecting following models, please contact Technical Helpdesk to clarify the additional charge.
PEFY-M50/63VMA(L)-A1
PEFY-MS71VMA(L)-A1
PLFY-50/63VEM6-E
PLFY-M71VEM6-E

## System Operation
COOLING OPERATION
Outdoor Unit | SYMBOL | F | TH4 | TH7 | 63LS | 63HS1 | MAIN BC BOX | SYMBOL | SC 16 MASTER | SH 12 MASTER | PS1 | PS3
| DESCRIPTION | Compressor Frequency | Compressor Discharge | Air or Water Inlet Temp | Low Pressure | High Pressure |  | DESCRIPTION | Intermediate Subcooling | Bypass Outlet Superheat | High Pressure | Intermediate Pressure
| DIPSWITCH | SW4 - 4, 5 + 7 ON | SW4 - 1, 3, 4 + 6 ON | SW4 - 1, 2, 3, 4 +7 ON | SW4 - 1, 2, 4, 5, + 6 ON | SW4 - 2, 4, 5, + 6 ON |  | DIPSWITCH | SW4 - 2, 3, 7 + 8 ON | SW4 - 1, 3, 7 +8 ON | SW4 - 2, 7 +8 ON | SW4 - 1, 2, 7 +8 ON
| Outdoor Unit 1 | [6 empty] | MAIN BC
Outdoor Unit 2
Outdoor Unit 3
HEATING OPERATION
Outdoor Unit | SYMBOL | F | TH4 | TH7 | 63LS | 63HS1 | MAIN BC BOX | SYMBOL | SC 16 MASTER | SH 12 MASTER | PS1 | PS3
| DESCRIPTION | Compressor Frequency | Compressor Discharge | Air or Water Inlet Temp | Low Pressure | High Pressure |  | DESCRIPTION | Intermediate Subcooling | Bypass Outlet Superheat | High Pressure | Intermediate Pressure
| DIPSWITCH | SW4 - 4, 5 + 7 ON | SW4 - 1, 3, 4 + 6 ON | SW4 - 1, 2, 3, 4 +7 ON | SW4 - 1, 2, 4, 5, + 6 ON | SW4 - 2, 4, 5, + 6 ON |  | DIPSWITCH | SW4 - 2, 3, 7 + 8 ON | SW4 - 1, 3, 7 +8 ON | SW4 - 2, 7 +8 ON | SW4 - 1, 2, 7 +8 ON
| Outdoor Unit 1 | [6 empty] | MAIN BC
Outdoor Unit 2
Outdoor Unit 3
MITSUBISHI VRF TYPE Y(S)XM-A OUTDOOR UNIT
OPERATING READINGS USING DIP SWITCHES SW4
NOTE 1: SW6 -10 MUST BE OFF FOR OUTDOOR READING
NOTE 2: SW6-9 MUST BE ON FOR MAIN BC READINGS