## Method Statements
METHOD STATEMENTS
Method Statement 1 Strength & Leak Test
5 Steps
| Step 1 | 3 bar (N2) | Minimum of 3 Minutes
| Step 2 | 15 bar (N2) | Minimum of 3 Minutes
| Step 3 | 32 bar (N2) | Minimum of 3 Minutes
| Step 4 | 41.5 bar (N2) | Strength test for a period of time that is acceptable to show any signs of deformation to the pipe work.
| Step 5 | 33 bar (N2) | After step 4, drop pressure to 33 bar for the final air tight test. The pressure should be held for a minimum of 24 hours. Taking into account the ambient temperatures across the 24 hours.
Method Statement 2 Triple Evacuation
6 Steps
| Step 1 | Evacuate the system to 10 Torr from both service valves. System manifold gauges must not be used to measure vacuum. A Torr gauge must be used at all times.
| Step 2 | Break the vacuum with OFN (N2) into "suction" service valve till 1 bar has registered at the "discharge" valve.
| Step 3 | Evacuate to 5 Torr from "discharge" valve.
| Step 4 | Repeat step 2. Then continue to step 5.
| Step 5 | Evacuate through both service valves to lowest pressure vacuum pump will achieve (Below 2 Torr for 1 hour minimum)
| Step 6 | Pressure Rise Test must then be carried out for a minimum of 15 minutes. If the pressure rises on the Torr gauge repeat steps 2 and 5 till no rise is detected.

## System Details
Contractor and Site Details
Installation Contractor Name and Address |  | Site Name and address
We hereby confirm that the systems logged in this book have been pressure tested and evacuated in accordance with the Mitsubishi Electric Method Statements 1 and 2
Note: All sections must be completed for acceptance by MEUK
| Commissioning Engineer | Date
Notes

## Systems
Indoor Unit Location Room Name | Indoor Unit Model | Indoor Serial Number | Outdoor Unit Location | Outdoor unit Model | Ourdoor Unit Serial Number | Address SW12 | Address SW11 | Inlet Cooling or TH21 from Monitor Tool | Outlet Cooling or TH22 from Monitor Tool | Inlet Heating or TH21 from Monitor Tool | Outlet Heating or TH22 from Monitor Tool | Piping Length in meters (One way) | Additional Charge in kgs